## BOQ
ALLO TECHNOLOGY SDN BHD PROCUREMENT UNIT
TITLE
REQUEST FOR QUOTATION ( RFQ ) FOR RENTING OF GENERATOR SET ( GENSET ) FOR ALLO CABIN AT PENCAWANG MASUK UTAMA SEDENAK ( PMU SEDENAK )
BILL OF QUANTITY
No. | Description | U.O.M. | Quantity | Price/Unit | Total (RM)
A | SCOPE OF WORK ( SOW )
1 | Rental of 20kVA 3 Phase Diesel Generator Set c/w power cable connection from Genset to ALLO Cabin PMU Sedenak (SDNK) | Month | 4 |  | 0
Site Location : ALLO Cabin PMU Sedenak ( Latitude Longitude : 1.700360, 103.416817 )
Operating hours : 24 hours / 7 days a week continuous runtime
* Genset vendor to responsible for the quality and adequacy of the genset supply and for the timely delivery of the services in accordance with the standards and specifications
Full rental service coverage including :
a | Application to Jabatan Alam Sekitar (DOE) and Suruhanjaya Tenaga (ST) for genset Installation
b | Transportation c/w installation and demobilisation charges to and from site
c | Diesel Refuelling, Schedule and unscheduled maintenance
d | 24 hours 7 days on-call emergency standby and on-site manpower support services for uninterrupted operations
e | Insurance - Contractor All Risk ( CAR ) & Workmenship Compensation ( WC )
f | Initial engagement is for 4 months, with extension / cancelation subject to Allo’s discretion.
g | Monthly CO² Emission Monitoring & Reporting
B | TENDER PRE-QUALIFIED CRITERIA
1 | Established genset supplier with a proven track record and the company must have minimum no. of three (3) years of experience in the industry
2 | The genset supplier must have their own generator set assets and must have a regional or state setup.
3 | Have a valid CIDB registration certification of Tenderer or Sub-contractors with minimum Grade G3 specialization in E04 (Low Voltage Installation and E32 (Low Voltage Generation)
4 | Have a valid registration certificate of the Tenderer or Sub-contractors with Suruhanjaya Tenaga (ST) as Electrical Contractor (Borang Q).
C | TECHNICAL REQUIREMENTS AND SPECIFICATIONS
1 | Generator Set Specification for ALLO ACNS Cabin Sites
A | Generator Design - 20kVA silent-type genset. The full load output voltage of the genset shall be 415 volts, 3 phase, 4 wires, 50 Hz ± 0.25% with neutral solidly earthed. Diesel engine directly coupled with a 4 pole 3 phase Alternator
B | Engine Rating - Prime Rated Power for Mutual standby and Standby Power for standby application according to comply BS 649 or equivalent standard.
D | SERVICE LEVEL AGREEMENT (SLA) REQUIREMENTS
To ensure minimal service disruption, the following SLA terms shall apply:
1 | Response Time : Vendor must respond within 30 minutes upon notification of genset supply outage
2 | Delivery Time : Replacement Genset to be delivered and operational at site within 2 hours
3 | Uptime Guarantee : Genset must operate continuously ( 24/7 ) without interruption during the rental period. Vendor must provide backup unit within 2 hours in case of failure
4 | Support Availability : 24/7 support and hotline to be provided
5 | Preventive Maintenance : Vendor responsible for diesel fuel top-up and maintenance during rental period
6 | Reporting : Monthly usage report and log sheet to be submitted for rental claims
SST 6% (RM)
GRAND TOTAL PRICE INCLUSIVE OF ALL APPLICABLE TAXES (RM) |  |  |  | 0
Compliance
Bil | Term & Conditions |  |  | Yes | No
1 | Payment Term : 45 days upon document verification and acceptance by Allo. (refer Appendix of POTC for milestone payment term) - Other terms please refer the POTC and the Appendix - Insurance - Refer POTC
2 | Commencement of works: 2 weeks upon PO issuance - Target to complete GENSET deployment by 2nd week of February 2026
3 | All work must comply with Suruhanjaya Tenaga (ST) and TNB standards. Contractor is responsible for all safety and coordination during the work period
6 | Other terms please refer the POTC and the Appendix
I acknowledge that I have read, understand and comply to the above job description in its entirety and capable of performing all of the stated requirements:
Signature:
Company Name:
Name:
Email:
Phone No:
Company stamp:
Date: