## Commercial
ALLO TECHNOLOGY SDN BHD
PROCUREMENT UNIT
Appendix A
RFQ: | Supply, Deliver, Install and Commissioning ten (10) units of 19inch Rack Mounted 48VDC Power System - Type 1 : 12kW and one (1) unit of 48VDC Battery System.
No. | Description | Recommended Brand | U.O.M. | Quantity | Price/Unit | Total (RM)
A | DC Power System
A1 | 48VDC SWITCHMODE RECTIFIER ( SMR ) SYSTEM
A1-1 | Supply, Installation and Commissioning of 19 Inch Rack Mounted 48VDC Power system - Type 1 : 12kW (Without 19 inch Equipment Perforated Rack) The rate shall inclusive of supply, installation, test & commissioning a complete 48VDC Power System (inclusive of 12kW Switchmode Rectifier (SMR) system, 2 x 3000W High Efficiency Rectifier Module (1+1) with 2 empty slot for future expansion up to max 12kW ( 4 x 3000W Rectifier Module ), SMR controller and monitoring unit, DC load circuit breaker - For Backup Battery : 2 x 100A MCB ( DC Type ), For Load : 2 x 63A MCB ( DC Type ), 3 x 16A MCB ( DC Type ), power cable connection c/w accessories from power source to SMR up to 10 meter (1 x 4C 16mm.sq. Cu/PVC/SWA/PVC ), Integration of SMR and battery alarm/monitoring parameters into ALLO’s LibreNMS platform (via SNMP or compatible protocol), transportation to site and any other related items to complete the installation according to ALLO specifications. | ELTEK / EXICOM / ZTT / ENETEK *Please circle the proposed brand. | Set | 10 |  | 0
Site Location :
1 ) Dayone Nusajaya Tech Park ( NTP ) Data Centre : 2 Set for Network Equipment Power A & Power B
2 ) TM Iskandar Puteri Data Centre ( TMIPDC ) : 2 Set for Network Equipment Power A & Power B
3 ) Kempas Tech Park ( KTP ) Data Centre : 2 Set for Network Equipment Power A & Power B
4 ) ZData Bridge Data Centre ( BDC ) Campus 2 : 2 Set for Network Equipment Power A & Power B
5 ) ZData Bridge Data Centre ( BDC ) Gelang Patah : 2 Set for Network Equipment Power A & Power B
A2 | 48VDC BATTERY BACKUP SYSTEM
A2-1 | Supply, Install and Commissioning of 48VDC Battery System (Type 1 - 100Ah LiFePO4 Battery Bank) This rate shall include all the cost to supply, install, test and commission a compact 48VDC battery bank, including the supply and installation of DC cables from SMR system to battery bank, transportation to site and supply and installation of other related accessories (including and not limited to MCB, fused switch, isolator etc) to complete the installation according to ALLO specifications. | EXICOM / SACRED SUN / ZTT / SUNWODA *Please circle the proposed brand. | Set | 1 |  | 0
Site Location :
1 ) Dayone Nusajaya Tech Park ( NTP ) Data Centre : 1 Set for Power A Backup Power
GRAND TOTAL PRICE INCLUSIVE OF ALL APPLICABLE TAXES (RM) |  |  |  |  | 0
REMARKS
1) Tenderer to submit full product specifications, test certificates and relevant supporting documents.
2) The Switch Mode Rectifier ( SMR ) and Backup Battery parameter must be integrated and accessible for remote monitoring by the Allo Network Operations Center ( NOC ). The LibreNMS SMR coding and scripting required for the integration must be pre-developed and successfully tested
3) In order to ensure effective stock management and standby readiness for Allo’s operational requirements, we recommend that only the following reputable incumbent brands be allowed under this RFQ for: - > Item A1 - 48VDC SWITCHMODE RECTIFIER ( SMR ) SYSTEM : ELTEK, EXICOM, ZTT and ENETEK - > Item A2 - 48VDC BATTERY BACKUP SYSTEM : EXICOM, SACRED SUN, ZTT and SUNWODA
4) This measure aims to streamline technical support, ensure component compatibility, and enable faster deployment in the event of urgent operational needs
5) All work must comply with Suruhanjaya Tenaga (ST) and TNB standards. Contractor is responsible for all safety and coordination during the work period.
6) The above price shall include delivery costs and all applicable taxes.
Compliance
Payment Term : 45 days upon document verification and acceptance by Allo. (refer Appendix of POTC for milestone payment term). - Other terms please refer the POTC and the Appendix. - Insurance - Refer POTC | [5 empty] | Yes/No
Commencement of works: Two (2) weeks upon PO issuance Completion date: One (1) month upon PO issuance | [5 empty] | Yes/No
I acknowledge that I have read, understand and comply to the above job description in its entirety and capable of performing all of the stated requirements:
Company Name:
Name:
Email:
Phone No:
Company stamp:
Date: