## Commercial
ALLO TECHNOLOGY SDN BHD
PROCUREMENT UNIT
Appendix A
RFQ: | SUPPLY, DELIVER, INSTALLATION AND COMMISSIONING OF ELEVEN (11) UNITS NETWORK INTERFACE DEVICE (NID) OUTDOOR CABINET IN PENINSULAR MALAYSIA
No. | Description | U.O.M. | Quantity | Price/Unit | Total (RM)
1 | Supply & installation of NID Outdoor Cabinet, main equipment, cabinet enhancement auxiliaries, , testing & commissioning, manpower, transportation to site, M&E works, civil works including plinth construction or concrete pole installation, and any other related items to complete the installation according to ALLO specifications. This NID Outdoor Cabinet shall comply with BOQ and ALLO technical specifications requirement provided and not limited to authority specifications and requirement. | EA | 11 |  | 0
Compulsory Requirements:
*Tenderers are required to comply with the Technical Compliance requirements set out in Appendix 1.
Site Location :
*Delivery shall be made to eleven (11) locations within Negeri Sembilan, in accordance with the attached Site Details List (Appendix 2).
SST (RM)
GRAND TOTAL PRICE INCLUSIVE OF ALL APPLICABLE TAXES (RM) |  |  |  |  | 0
REMARKS
1) Tenderer to submit full product specifications, test certificates and relevant supporting documents.
2) The Switch Mode Rectifier ( SMR ) and Backup Battery parameter must be integrated and accessible for remote monitoring by the Allo Network Operations Center ( NOC ). The LibreNMS SMR coding and scripting required for the integration must be pre-developed and successfully tested
3) In order to ensure effective stock management and standby readiness for Allo’s operational requirements, we recommend that only the following reputable incumbent brands be allowed under this RFQ for: - > Item A1 - 48VDC SWITCHMODE RECTIFIER ( SMR ) SYSTEM : ELTEK, EXICOM, ZTT and ENETEK - > Item A2 - 48VDC BATTERY BACKUP SYSTEM : EXICOM, SACRED SUN, ZTT and SUNWODA
4) This measure aims to streamline technical support, ensure component compatibility, and enable faster deployment in the event of urgent operational needs
Compliance
Payment Term : 45 days upon document verification and acceptance by Allo. (refer Appendix of POTC for milestone payment term). - Other terms please refer the POTC and the Appendix. - Insurance - Refer POTC |  |  |  |  | Yes/No
Commencement of works: Two (2) weeks upon PO issuance Completion date: One (1) month upon PO issuance |  |  |  |  | Yes/No
I acknowledge that I have read, understand and comply to the above job description in its entirety and capable of performing all of the stated requirements:
Company Name:
Name:
Email:
Phone No:
Company stamp:
Date:

## Technical Compliance -Appendix1
APPENDIX 1
TECHNICAL COMPLIANCE : SUPPLY, INSTALLATION AND COMMISSIONING OF NID OUTDOOR CABINET IN PENINSULAR MALAYSIA
| No. | Description
Supply & installation of NID Outdoor Cabinet, main equipment, cabinet enhancement auxiliaries, , testing & commissioning, manpower, transportation to site, M&E works, civil works including plinth construction or concrete pole installation, and any other related items to complete the installation according to ALLO specifications. This NID Outdoor Cabinet shall comply with BOQ and ALLO technical specifications requirement provided and not limited to authority specifications and requirement.
|  | 1 | Compulsary Requirement for NID Outdoor Cabinet ( NID ODC ) and Auxiliaries | Compliance (Yes/No) | Remarks and References
|  | A | Enclosure
|  | 1 | Cabinet Type : Outdoor Weatherproof, Front door access only
|  | 2 | IP Rating : IP55, Sealed cabinet , No Dust entrance
|  | 3 | Floor Standing type Cabinet Dimension : Height : 1100 mm x Width : 600 mm x Depth : 450 mm
Pole Mounted type Cabinet Dimension : Height : 800 mm x Width : 600 mm x Depth : 450 mm
|  | 4 | Installation mode : Floor standing, mounted against plinth / Pole mounted
|  | 5 | Material Specifications : 2mm Electro-galvanised (E.G) Steel Sheet ( JIS G3313 SECC-P or equivalent )
|  | 6 | Coating Powder : Thickness of coat 3-5 g/m² with Anti Rust
|  | 7 | Finishing : RAL 7035 Epoxy powder coated. Painted grey background with ALLO logo at the front (size of logo is approximately 30cm x 30cm)
|  | 8 | Heat management System : Free Cooling Unit (FCU) c/w min. G4 /M6 air filter, temperature monitoring and variable fan speed controller (IP 55 compliance)
|  | 9 | Operating Temperature : Typical < 45°C @ 10% allowance time occur and at 45°C and above shall not exceed 1 hour
|  | 10 | Equipment Rack : 19" Rack ( 15U ) ( Able to fit standard 19 telecommunication equipment such as TM NID, Fiber ODF, Switch Mode Rectifier ( SMR )
|  | 11 | Security : Minimum 3-point per door locking systems ( stainless steel door handle ) with padlock earpiece and padlock protection cover for 50mm padlock, Enhanced with 75mmx75mmx6mm galvanised security lock bar / belting with padlock earpiece and padlock protection cover for 50mm padlock.
|  | 12 | Cable Access : From bottom of cabinet by Waterproof Cable Connector Gland ( 5xPG16 - Power and Grounding Cable & Optical Cable )
|  | 13 | To provide proposed engineering drawings for all of the above during tender submission
Cabinet Enhancement Assembly
|  | 1 | 1 unit of Cabinet Service Lamp ( 48VDC )
|  | 2 | 1 unit of Anti-theft Accessories ( Door Sensor - Limit switch SPDT Roller Lever )
|  | 3 | PRO COLEX 50mm Brass Body, Anti-Cut Padlock, Stainless steel cap c/w key set
|  | 4 | Tenderer to submit proposed drawing / product specifications / catalog for all of the above during tender submission
|  | B | AC Power system - AC Power Distribution Board ( ACPDB )
|  | 1 | Power Supply Mode : Single Phase 230V AC, 50Hz
|  | 2 | ACPDB Type : 19 inch rack mounted ( 5U )
|  | 3 | AC Input Breaker : 16A 2 Pole MCB 10kA, 40A 100mA 2 Pole RCCB type 'A' c/w Automation Restoration System ( ARS )
|  | 4 | AC Surge Protection Device ( SPD ) : 1+1 Stage 2 Protection ( L-N , N-PE ), Metal Oxide Varistor ( MOV ), Pluggable, Imax : 40kA @ 8/20us
|  | 5 | AC Output Breaker : Rectifier : 10A 1 Pole MCB 10kA, Spare & Ventilation System : 6A 1 Pole MCB 10kA
|  | 6 | Accessories : 6 ways neutral (black ) & earth (green) link c/w insulated mounting bracket,
|  | 7 | All components and system cabling must comply to the relevant standards ( SIRIM / IEEE / IEC / EN or equivalent)
|  | C | DC Power system - Switch Mode Rectifier System
|  | 1 | Type : 1.8kW Switch Mode Rectifier (SMR) c/w monitoring control unit (MCU), BLVD & LLVD, temperature sensors, N+1 configuration and all necessary accessories
|  | 2 | Rectifier Module : 900W High Efficiency ( > 95% ), 1+1 Configuration
|  | 3 | Warranty : 2 years warranty not limited to labour & related accessories against any defects
|  | 4 | Housekeeping Alarms : Required for monitoring of anti-theft, high temperature, AC supply input detection & 48VDC SMR system general alarm contact
|  | 5 | DC Load Circuit Breaker : For Backup Battery : 2 x 30A 1P MCB ( DC Type ), For Load : 2 x 10A 1 Pole MCB ( DC Type ), 2 x 16A 1 Pole MCB ( DC Type )
|  | 6 | Integration of SMR rectifier alarm parameters into LibreNMS ( ALLO NOC ) : Rectifier, battery, and external alarms
DC Power system - Backup Battery
|  | 1 | Battery type & capacity : 10Ah Lithium Ion ( LiFePo4 ) Battery with nominal system voltage of -48 Vdc to backup the power required for equipments
|  | 2 | Battery Brand ,Model & Country of origin : Tenderer to state
|  | 3 | Design Life : Minimum 10 years / Warranty : 2 years warranty and maintenance free: including and not limited to labour & related accessories against any defects
|  | 4 | Status Indicator : With LED status and lithium battery BMS shall be able to integrate to rectifier system for monitoring and control
|  | 5 | DC Battery Cables : All Power and Earthing Cables sizing calculation must comply to IEEE/IEC 60364 requirements
|  | D | Equipment - Optical Fiber Distribution Hub
|  | 1 | 19" rack mounted 12 ports Optical Distribution Frames ( ODF ) c/w SC/APC connector c/w pig-tails ( 5 Meter max. length ) for up to 100% of the ODF capacity
|  | 2 | Compulsary Requirement for Civil Works, Installation Material, Engineering and installation services
|  | A | Preliminary
|  | 1 | Technical site survey for site location and site design confirmation and Preparation of Technical Proposal & Drawing
| 2 |  | To Perform and Document Underground Mapping Detection for Utilities
|  | 1 | The rate is inclusive of every related services for Utility Mapping until commissioning, with provided equipment calibration cert, manpower, transportation to site, different spray colour for different utilities, pegging marking with stick wood and spray to mark a proposed location for NID Outdoor Cabinet installation and any other related items to complete the installation according to ALLO specifications.
Power & Fiber Optic Cable Connectivity
|  | 1 | Supply and install 1 x 3C 2.5mm² Cu/PVC/SWA/PVC power cable c/w 1 inch Galvanized Iron ( G.I ) pipe and accessories ( Length : 10 Meter ) - Burried from NID ODC to Meter Panel at ALLO C-Side Pole
|  | 2 | Electrical installation, cable termination and commissioning by Wireman PW2 from TNB kwh metering Panel to ACDB inside NID Outdoor cabinet
|  | 3 | Supply and install SC-SC Armored Fiber Drop Cable Single Mode Patch Cord c/w 1 inch Galvanized Iron ( G.I ) pipe and accessories ( Length : 20 Meter ) - Burried from NID ODC to OLT Panel at ALLO C-Side Pole
|  | B | Details of Plinth (Concrete Pedestal) for NID Outdoor Cabinet
|  | 1 | For Floor Standing type : Construct Pre-cast Concrete G30 Plinth 500mm thickness x 650mm width x 300mm height for NID outdoor cabinet. Scope inclusive of excavate and levelling, lean concrete and 100mm HDPE double wall corrugated pipe for underground cable access from NID outdoor cabinet to 18" X 18" X 18" telecommunications pit (1 way)
|  | 2 | For Pole Mounted type : Supply and install 9 meter concrete spun pole with proper necessary accessories. Scope inclusive of excavate and 100mm HDPE double wall corrugated pipe for underground cable access from NID outdoor cabinet to 18" X 18" X 18" telecommunications pit (1 way)
|  | 3 | Supply and install 18" X 18" X 18" telecommunications pit complete set c/w pit cover
|  | 4 | To provide proposed engineering drawings for all of the above during tender submission
Details of Grounding system for NID Outdoor Cabinet
|  | 1 | Minimum grounding resistance requirement : less than 5 Ohm
|  | 2 | Supply and install heavy duty concrete earth chamber
|  | 3 | Supply and install 12mm x 1500mm copper earth rods c/w rod coupling and drive into the earth using a compactor / vibrator
|  | 4 | Supply and install 25mm x 3mm copper tape ( Length : 15 meter )
|  | 5 | Supply, install and terminate 1x16 mm.sq insulated steel cable from grounding electrode to earthing terminal c/w accessories
|  | 6 | Supply and Install exotermic welding between conductor to copper earth rod and 25mmx3mm copper tape and copper earth rod
|  | C | Installation Material, Engineering and installation Service
|  | 1 | Cabinet delivery services
|  | 2 | Engineering services required / Delivery accessories per cabinet assembly
|  | 3 | Cabinet integration to Concrete pedestal / plinth with proper sealant and waterproofing
|  | 4 | Mobilisation ( Refer to Additional Compulsary Requirement - Item 7 and Site List )
Documentation and Hand-Over Details
|  | 1 | This rate is inclusive for documentation with as-built details. A complete set of report consist but not limited to Technical Proposal, Technical Drawing, Document of Submission to Local Authorithy for permitting, Document of Power Supply Application, Datasheet of every Active and Passive Component installed. This report shall be submitted in hard-copy and soft-copy which a copy of KMZ, Cad, Excel and PDF are to be compiled in a one(1) hard-drive.
ALLO TENDER TECHNICAL DRAWING :-
|  | 1 | PROPOSE INSTALLATION, ELECTRICAL SCHEMATICS AND DIMENSION LAYOUT DIAGRAM FOR NID OUTDOOR CABINET ( NID ODC ) ON GROUND - FLOOR STANDING TYPE : ALLO/ODC/TMNID/1
|  | 2 | PROPOSE INSTALLATION, ELECTRICAL SCHEMATICS AND DIMENSION LAYOUT DIAGRAM FOR NID OUTDOOR CABINET ( NID ODC ) ON POLE - POLE MOUNTED TYPE : ALLO/ODC/TMNID/2
REMARKS
|  | 1 | Tenderer to submit full product specifications, test certificates and relevant supporting documents.
|  | 2 | The Switch Mode Rectifier ( SMR ) and Backup Battery parameter must be integrated and accessible for remote monitoring by the Allo Network Operations Center ( NOC ). The LibreNMS SMR coding and scripting required for the integration must be pre-developed and successfully tested
|  | 3 | In order to ensure effective stock management and standby readiness for Allo’s operational requirements, we recommend that only the following reputable incumbent brands be allowed under this RFQ for
> Item 1-C - 48VDC SWITCHMODE RECTIFIER ( SMR ) SYSTEM : ELTEK, EXICOM, ZTT and ENETEK
> Item 1-C - 48VDC BATTERY BACKUP SYSTEM : EXICOM, SACRED SUN, ZTT and SUNWODA
|  | 4 | This measure aims to streamline technical support, ensure component compatibility, and enable faster deployment in the event of urgent operational needs
Additional Compulsary Requirement to Comply:
|  | 1 | All the materials ( Except DC Power system - Rectifier & Battery ) and services provided must come with a minimum of twelve (12) months warranty. The warranty date will commence on the date of commissioning as accepted by ALLO. A minimum of twelve (12) months warranty period for this should cover both the materials and workmanship/services provided.
|  | 2 | Appointed Quotationer is expected to prepare the all the materials by 14 days after ALLO issue a Purchase Order (PO). This PO will be issued by email from ALLO-Procurement.
|  | 3 | Appointed Quotationer is expected to deliver all the materials, installation, services and to make sure sites capable of Ready-for-Service (RFS) by 14 days after received email from project team ( Network - CME ) to start for construction and cabinet deployment.
|  | 4 | The Appointed Quotationer shall be responsible for the submission of all Plant for site tests and inspection as required by the ALLO. During the course of equipment installation and implantation of civil infrastructure, ALLO shall inspect the progress of the work and check the workmanship and accuracy. On completion of the work prior to commissioning of materials, cables and any related item supplied shall be tested to the satisfaction of ALLO to demonstrate that it is entirely suitable for commercial operation. The Appointed Quotationer shall provide all equipment, test gear, materials and labor required to perform the site acceptance test. Provision of suitable test gears and their calibrations for the test is the responsibility of the Appointed Quotationer. All tests shall be witnessed and approved by the ALLO’s technical person. Any item of plant or component which fails to comply with the ALLO’s expected test results or the technical requirement in any respect whatsoever at any stage of manufacture, test, installation or commissioning, may be rejected by the ALLO either in whole or in part as the ALLO considers necessary.
|  | 5 | Quotationer may refer to document in attachment included, and quotationer may propose a different brand but to comply with the equivalent technical capability and sizes.
|  | 6 | The rejected plant shall be replaced by the Appointed Quotationer at their own expense and to the satisfaction of the ALLO.
|  | 7 | For the purpose of Mobilisation to sites, sites location will be at ( To be notify by project team ( Network - CME ) to vendor in 14 days before sites deployment ): i) Northern Region : Perak, Pulau Pinang, Kedah, Perlis ii) Southern Region : Negeri Sembilan, Johor
I acknowledge that I have read, understand and comply to the above job description in its entirely and capable of performing all of the stated requirements:
Signature:
Name :
Designation :
Company Name :
Company's Stamp :
Date :

## Site List - Appendix2
APPENDIX 2

## Proposed Diagram - Appendix3
APPENDIX 3